{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["iec104_analogue","iec104_digital","iec104_commands"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"iec104_analogue","index":0,"n_rows":57,"n_cols":10,"rows_kept":57,"cut":false,"hidden":false,"merged":[]}
["address","type","data","interrogation","spontaneous","cyclic","absmin","absmax","rel","desc"]
[1000,"M_ME_TF_1","section.rms_current","global",true,true,10,100,10,"RMS current [A]"]
[1001,"M_ME_TF_1","section.rms_voltage","global",true,true,10,100,10,"RMS voltage [kV]"]
[1002,"M_ME_TF_1","section.power_factor","global",true,true,10,100,10,"Power factor [-1;1]"]
[1003,"M_ME_TF_1","section.rms_apparent_power","global",true,true,10,100,10,"Apparent power |S| [kVA]"]
[1004,"M_ME_TF_1","section.rms_reactive_power","global",true,true,10,100,10,"Reactive power Q [kVAr]"]
[1005,"M_ME_TF_1","section.rms_real_power","global",true,true,10,100,10,"Real power P [kW]"]
[1006,"M_ME_TF_1","section.thd_current","global",true,true,10,100,10,"Total Harmonic Distortion of the current [percent]"]
[1007,"M_ME_TF_1","section.thd_voltage","global",true,true,10,100,10,"Total Harmonic Distortion of the voltage [percent]"]
[1011,"M_ME_TF_1","section.main_harmonic_frequency","global",true,true,10,100,10,"The main harmonic frequency of the master measurement channel [Hz]"]
[1200,"M_ME_TF_1","state.estimator_error","global",true,true,10,100,10,"Estimator error of the automatic calibration model"]
[1201,"M_ME_TF_1","state.resource_alert","global",true,true,10,100,10,"Warning of low amount of RAM or flash memory available (=1 if triggered)"]
[1202,"M_ME_TF_1","state.processor_temperature","global",true,true,10,100,10,"The core temperature of the processor [degrees Celcius]"]
[10000,"M_ME_TF_1","phase01.rms_current","global",true,true,10,100,10,"RMS current [A]"]
[10001,"M_ME_TF_1","phase01.rms_voltage","global",true,true,10,100,10,"RMS voltage [kV]"]
[10002,"M_ME_TF_1","phase01.power_factor","global",true,true,10,100,10,"Power factor [-1;1]"]
[10003,"M_ME_TF_1","phase01.rms_apparent_power","global",true,true,10,100,10,"Apparent power |S| [kVA]"]
[10004,"M_ME_TF_1","phase01.rms_reactive_power","global",true,true,10,100,10,"Reactive power Q [kVAr]"]
[10005,"M_ME_TF_1","phase01.rms_real_power","global",true,true,10,100,10,"Real power P [kW]"]
[10006,"M_ME_TF_1","phase01.thd_current","global",true,true,10,100,10,"Total Harmonic Distortion of the current [percent]"]
[10007,"M_ME_TF_1","phase01.thd_voltage","global",true,true,10,100,10,"Total Harmonic Distortion of the voltage [percent]"]
[10008,"M_ME_TF_1","phase01.phase_current","global",true,true,10,100,10,"Phase of the current with respect to the sensor master reference [degrees]"]
[10009,"M_ME_TF_1","phase01.phase_delta","global",true,true,10,100,10,"Phase difference between voltage and current ; leading voltage is positive [degrees]"]
[10010,"M_ME_TF_1","phase01.phase_voltage","global",true,true,10,100,10,"Phase of the voltage with respect to the sensor master reference [degrees]"]
[11000,"M_ME_TF_1","phase02.rms_current","global",true,true,10,100,10,"RMS current [A]"]
[11001,"M_ME_TF_1","phase02.rms_voltage","global",true,true,10,100,10,"RMS voltage [kV]"]
[11002,"M_ME_TF_1","phase02.power_factor","global",true,true,10,100,10,"Power factor [-1;1]"]
[11003,"M_ME_TF_1","phase02.rms_apparent_power","global",true,true,10,100,10,"Apparent power |S| [kVA]"]
[11004,"M_ME_TF_1","phase02.rms_reactive_power","global",true,true,10,100,10,"Reactive power Q [kVAr]"]
[11005,"M_ME_TF_1","phase02.rms_real_power","global",true,true,10,100,10,"Real power P [kW]"]
[11006,"M_ME_TF_1","phase02.thd_current","global",true,true,10,100,10,"Total Harmonic Distortion of the current [percent]"]
[11007,"M_ME_TF_1","phase02.thd_voltage","global",true,true,10,100,10,"Total Harmonic Distortion of the voltage [percent]"]
[11008,"M_ME_TF_1","phase02.phase_current","global",true,true,10,100,10,"Phase of the current with respect to the sensor master reference [degrees]"]
[11009,"M_ME_TF_1","phase02.phase_delta","global",true,true,10,100,10,"Phase difference between voltage and current ; leading voltage is positive [degrees]"]
[11010,"M_ME_TF_1","phase02.phase_voltage","global",true,true,10,100,10,"Phase of the voltage with respect to the sensor master reference [degrees]"]
[12000,"M_ME_TF_1","phase03.rms_current","global",true,true,10,100,10,"RMS current [A]"]
[12001,"M_ME_TF_1","phase03.rms_voltage","global",true,true,10,100,10,"RMS voltage [kV]"]
[12002,"M_ME_TF_1","phase03.power_factor","global",true,true,10,100,10,"Power factor [-1;1]"]
[12003,"M_ME_TF_1","phase03.rms_apparent_power","global",true,true,10,100,10,"Apparent power |S| [kVA]"]
[12004,"M_ME_TF_1","phase03.rms_reactive_power","global",true,true,10,100,10,"Reactive power Q [kVAr]"]
[12005,"M_ME_TF_1","phase03.rms_real_power","global",true,true,10,100,10,"Real power P [kW]"]
[12006,"M_ME_TF_1","phase03.thd_current","global",true,true,10,100,10,"Total Harmonic Distortion of the current [percent]"]
[12007,"M_ME_TF_1","phase03.thd_voltage","global",true,true,10,100,10,"Total Harmonic Distortion of the voltage [percent]"]
[12008,"M_ME_TF_1","phase03.phase_current","global",true,true,10,100,10,"Phase of the current with respect to the sensor master reference [degrees]"]
[12009,"M_ME_TF_1","phase03.phase_delta","global",true,true,10,100,10,"Phase difference between voltage and current ; leading voltage is positive [degrees]"]
[12010,"M_ME_TF_1","phase03.phase_voltage","global",true,true,10,100,10,"Phase of the voltage with respect to the sensor master reference [degrees]"]
[13000,"M_ME_TF_1","phase04.rms_current","global",true,true,10,100,10,"RMS current [A]"]
[13001,"M_ME_TF_1","phase04.rms_voltage","global",true,true,10,100,10,"RMS voltage [kV]"]
[13002,"M_ME_TF_1","phase04.power_factor","global",true,true,10,100,10,"Power factor [-1;1]"]
[13003,"M_ME_TF_1","phase04.rms_apparent_power","global",true,true,10,100,10,"Apparent power |S| [kVA]"]
[13004,"M_ME_TF_1","phase04.rms_reactive_power","global",true,true,10,100,10,"Reactive power Q [kVAr]"]
[13005,"M_ME_TF_1","phase04.rms_real_power","global",true,true,10,100,10,"Real power P [kW]"]
[13006,"M_ME_TF_1","phase04.thd_current","global",true,true,10,100,10,"Total Harmonic Distortion of the current [percent]"]
[13007,"M_ME_TF_1","phase04.thd_voltage","global",true,true,10,100,10,"Total Harmonic Distortion of the voltage [percent]"]
[13008,"M_ME_TF_1","phase04.phase_current","global",true,true,10,100,10,"Phase of the current with respect to the sensor master reference [degrees]"]
[13009,"M_ME_TF_1","phase04.phase_delta","global",true,true,10,100,10,"Phase difference between voltage and current ; leading voltage is positive [degrees]"]
[13010,"M_ME_TF_1","phase04.phase_voltage","global",true,true,10,100,10,"Phase of the voltage with respect to the sensor master reference [degrees]"]

{"sheet":"iec104_digital","index":1,"n_rows":1,"n_cols":7,"rows_kept":1,"cut":false,"hidden":false,"merged":[]}
["address","type","data","interrogation","spontaneous","background","desc"]

{"sheet":"iec104_commands","index":2,"n_rows":1,"n_cols":5,"rows_kept":1,"cut":false,"hidden":false,"merged":[]}
["address","type","data","settings","desc"]